SIMULINK Model Structure of UW Meshed Microgrid

Figure 1 shows the UW Meshed Microgrid diagram.

Figure 1. Three Phase Diagram of UW Meshed Microgrid

Impedances of microgrid lines and transformers are listed in Table 1 and 2 respectively.

Table 1. Line impedances of UW meshed microgrid

| Line Impedance | Length [ft] | R [Ω] | XL [Ω] | XC [Ω] |
| --- | --- | --- | --- | --- |
| PC1 | 366 | 0.093400 | 0.025500 | 82.7 |
| PC2 | 18 | 0.002810 | 0.000679 | 2894.3 |
| PC3 | 175 | 0.027352 | 0.006600 | 288.6 |
| PC4 | 108 | 0.016880 | 0.004070 | 336.7 |
| PC5 | 17 | 0.002600 | 0.000640 | 2020.2 |
| PC6 | 75 | 0.013700 | 0.003300 | 577.2 |

Table 2. Transformer impedances of UW meshed microgrid

| Tag | Volt-Amp Rating | Impedance | HV Side Resistance[Ω] | HV Side Reactance[Ω] | LV Side Resistance[Ω] | LV Side Reactance[Ω] |
| --- | --- | --- | --- | --- | --- | --- |
| T1 | 2500 kVA | 5.50% | 0.04707123 | 0.1882849 | 0.000627 | 0.0025068 |
| T2 | 75 kVA | 4.40% | 0.01689600 | 0.0675840 | 0.003173 | 0.0126908 |
| T3 | 45 kVA | 4.20% | 0.02688000 | 0.1075200 | 0.005047 | 0.0201899 |
| T4 | 45 kVA | 4.20% | 0.00671900 | 0.0268800 | 0.005047 | 0.0201899 |
| T5 | 45 kVA | 4.20% | 0.02688000 | 0.1075200 | 0.005047 | 0.0201899 |

Table 3. Loads of UW meshed microgrid

| Tag | Power Rating |
| --- | --- |
| L11-L12 | 4 kW |
| L21-L22 | 4 kW |
| L31-L32 | 4 kW |
| L41-L42 | 4 kW |

The parameters which belong to Microsource (MS), Microsource with energy storage (ES) and GENSET are listed in Table 4, 5 and 6, respectively.

Table 4. MS parameters

| VDC | 750 V |
| --- | --- |
| SBASE | 15 kVA |
| VBASE | 208 V |
| ωbase | 376.9911 (2π60) |
| (ω | 3.1416 (2π0.5) |
| Pmax | 15 kW (1 pu) |
| Pmin | 0 kW |
| Preq | 4 kW (0.2667 pu) |
| Vreq | 208 V (1 pu) |
| Kpp | 3 |
| Kpi | 30 |
| Kvp | 0.01 |
| Kvi | 5 |
| mQ | 0.05 |
| mP | 3.1416 |
| τVQP | 0.01 |

Table 5. ES parameters

| VDC | 750 V |
| --- | --- |
| SBASE | 15 kVA |
| VBASE | 208 V |
| ωbase | 376.9911 (2π60) |
| (ω | 3.1416 (2π0.5) |
| Pmax | 15 kW (1 pu) |
| Pmin | -2.5 kW (-0.1667 pu) |
| Preq | 4 kW (0.2667 pu) |
| Vreq | 208 V (1 pu) |
| Kpp | 3 |
| Kpi | 30 |
| Kvp | 0.01 |
| Kvi | 5 |
| mQ | 0.05 |
| mP | 2.6928 |
| τVQP | 0.01 |

The calculation of power-frequency slope, mP

mP for MS						mP for ES

Table 6. GENSET parameters

| SBASE | 12.5 kVA |  | ηthr | 0.47 |
| --- | --- | --- | --- | --- |
| VBASE | 208 V |  | Kev | 11.8238 |
| ωbase | 376.9911 (2π60) |  | Kfv | 3600 |
| (ω | 3.1416 (2π0.5) |  | τ | 0.022 |
| Pmax | 12.5 kW (1 pu) |  | Km | 0.36 |
| Pmin | 0 kW |  | τe | 0.001 |
| Vreq | 208V (1 pu) |  | Kvp | 1000 |
| Kpp | 3 |  | Kvi | 10 |
| Kpi | 30 |  | Kgp | 3 |
| mP | 3.1416 |  | Kgi | 4 |
|  |  | Ktf | 0.625 |

Table 7. Synchronous generator parameters

| xd | 1.204 |  | Td0’ | 0.35523 |
| --- | --- | --- | --- | --- |
| xd’ | 0.125 |  | Td0” | 0.00015 |
| xd” | 0.056 |  | Tq0” | 0.0067 |
| xq | 0.533 |  | Rs | 0.0217 |
| xq’ | 0.051 |  | H | 0.19 |
| xq” | 0.037 |  | p | 2 |

Case 1: Islanding

- On-Site load 28 kW:  Importing 18kW

- Island event at t=1.0sec

- Additional 4kW load (L22) at t=2.0sec

Case 2: Loss of cable PC3 in island operation

- On-Site load 32 kW:  Importing  0 kW

- Open cable at  t=1sec

Case 3 loss of Kohler in island operation

- On-Site load 32 kW:  Importing  0 kW

- Kohler lost at t=0 seconds

- Load: low frequency trip at frequency is 59 hZ at ~2.2 seconds.

- Trip 8 kW atBus-1 (L11&L12) and Bus -3 (L31&L32)

CASE1

ES: Set to -1kW of 15kW rating                 MS: Set to 5kW of 15kW rating                 GENSET: Set to 10kW of 12.5kW rating

CASE2

ES: Set to -1kW of 15kW rating                 MS: Set to 5kW of 15kW rating                 GENSET: Set to 10kW of 12.5kW rating

CASE3

ES: Set to -1kW of 15kW rating                 MS: Set to 5kW of 15kW rating                 GENSET: Set to 10kW of 12.5kW rating

CASE1                                                CASE2                                             CASE3

PC3

PC4

PC5

PC6

# Text boxes

Bus-2

From Outside Line

Kohler Genset (12.5 kW)

Micro-Source

Inverter based

(15 kW)

L31

L32

Bus-3

L42

L41

Bus- 4

L21

L22

L12

L11

Bus-1

Energy Storage (15 kW)

T2

PC1

SS

PC2

20yds

T1

T42

T3

PC6

25 yds

PC5

15yds

PC3

75yds

PC4

25yds

P4,Q4

P3,Q3

P5,Q5

P6,Q6